# NCP4 Compressor and Treatment Equipment Maintenance History

Extract date: 09 June 2026. This file contains the signed maintenance history used to reconcile stale equipment-register entries and treatment-equipment condition.

| Date | Asset | Event | Maintenance detail | Evidence | Engineering consequence |
| --- | --- | --- | --- | --- | --- |
| 2025-02-14 | C-102 | Motor failure corrective action | Original motor and fixed-speed starter removed. Installed 75 kW premium-efficiency motor and ABB ACS880 VSD package. Commissioned trim range: 500-1,200 Nm3/h. Direct drive kW tag enabled. | Signed work order WO-25-0214-C102 | Current configuration supersedes asset-register entry. |
| 2025-03-02 | C-102 | Controls follow-up | Legacy calculated load-percent tag retained in historian for trend continuity. It still multiplies load percentage by old 90 kW basis and must not be used as electrical energy evidence. | Controls note CN-25-0302 | Use direct C102_DRIVE_KW tag. |
| 2026-05-18 | C-103 | Separator inspection | High oil carryover and elevated separator differential pressure. Unit locked out pending separator replacement, downstream cleanup, and vendor return-to-service sign-off. | Signed lockout record LOTO-26-0518-C103 | C-103 unavailable. Do not count as standby or commissioning backup. |
| 2026-06-05 | DR-301 / F-301 | Dryer-filter inspection | Peak treatment-train differential pressure measured between 0.33 and 0.36 bar. Coalescing-filter service overdue. Purge solenoid suspected to leak above nameplate purge estimate. | Signed service inspection SI-26-0605 | Use 0.35 bar as-found peak drop for current-state pressure reconstruction; use serviced basis only for post-retrofit screening. |
| 2026-06-06 | C-101 | Routine inspection | No material defects. Fixed-speed load/unload unit remains available for base-load duty. | Routine inspection RI-26-0606 | Use as available base-load unit. |

# Open Maintenance and Commissioning Items

Confirm master-sequencer firmware compatibility with the proposed C-102 VSD integration module before purchase-order release.

Complete dryer/filter service and document post-service differential pressure during commissioning.

Do not return C-103 to standby duty until separator replacement, downstream cleanup, and vendor sign-off are complete.

Confirm safety-valve sizing and statutory inspection requirements for added receiver volume.

# Engineering Interpretation

The asset register is a legacy record and is not the source of truth where a later signed work order or lockout record establishes the installed configuration or current availability. For modelling, C-101 is the available base-load unit, C-102 is the available VSD trim unit, and C-103 is unavailable.